INSTALLATION INSTRUCTIONS FOR

EXTENSION USED ON

AMERICAN-DARLING® 4-1/2” MARK-73® & 5-1/4” B84B®

- Disassemble Fire Hydrant by:

  - Remove bolts and nuts holding upper barrel to lower barrel.

  - Remove the breakable barrel flange.

  - Turn the operating nut in the direction to open so that upper barrel can be separated from lower barrel.  Care must be taken to insure the main valve does not open.  This is accomplished by applying upward pressure on the upper barrel while turning the operating nut.

  - Remove the lower rod coupling pin and cotter pin when sufficient separation permits.

Note:  Care should be taken to insure the upper barrel cannot fall during the removal of lower rod coupling pin.

  - Upper barrel may now be removed.

- The Extension is now ready to be installed by:

- Assemble extension rod to large end of extension coupling using coupling pin and cotter pin.

- Now fasten the extension rod assembly to the lower rod through the second set of holes in the extension coupling using a second coupling pin and cotter pin.

- Clean any dirt, pieces of gasket, etc. from the machine surface of lower barrel and extension barrel.

- Place extension gasket on machine surface of lower barrel.

- Place extension barrel on top of lower barrel.  Care should be taken to insure flange gasket is in proper place and that the bolt holes between lower barrel and extension barrel are lined up.

- Fasten extension barrel to lower barrel using bolts provided with extension.

- The Fire Hydrant is now ready to be reassembled by:

  - Clean any dirt, etc. from machined surface of the extension barrel and bottom of upper barrel.

  - Install new flange gasket on extension barrel.

  - Place upper barrel above extension barrel and lower until hole in breakable rod coupling lines up with hole in rod extension.

  - Install coupling pin to connect breakable rod coupling to rod extension.

Note:  Care should be taken to insure the upper barrel cannot fall during the replacement of new coupling pin.

  - Turn operating nut in direction to close so that upper barrel will lower onto extension barrel.

Note:  Make sure the upper barrel is facing the desired direction.

  - Install breakable flange with existing bolts and nuts and tighten.

  - Check for gasket leaks by slightly unscrewing one nozzle cap and opening the hydrant valve until water starts to flow through the nozzle.  Close the cap and check for gasket leaks under pressure.  Close hydrant valve and open nozzle cap until the hydrant has drained, then retighten.

  - The fire hydrant is now ready for service.