INSTRUCTIONS FOR INSTALLING

TRAFFIC REPAIR KIT ON

AMERICAN-DARLING® 4-1/2” MARK-73® & 5-1/4” B84B® FIRE HYDRANTS

- Disassemble Fire Hydrant by:

  - Isolate the hydrant from the main water supply, if it hasn’t already been done.

  - Remove bolts and nuts that hold upper barrel to lower barrel.  The upper barrel may be completely separated due to vehicle impact.

  - Check all hydrant parts above ground to insure they are in good working condition.

  - Turn operating nut in the direction to open until upper rod coupling, coupling pin & cotter pin can be easily reached.

  - Remove and discard the cotter pin, coupling pin, and top half of the broken rod coupling.

  - Remove and discard the cotter pin, coupling pin, and bottom half of the broken rod coupling on the lower stem.

Note:  Care should be taken to prevent any of these parts from falling into the lower barrel.

  - Remove and discard barrel gasket and breakable flange halves.

Note:  The flange halves will probably be in several pieces.

- Reassemble Fire Hydrant by:

- Install the small end of the breakable rod coupling to the lower rod using new clevis pin and cotter pin.

- Clean any debris from machine surface of lower barrel.

- Install new flange gasket on lower barrel.

Note:  Care should be taken to insure flange gasket is centered over lower barrel surface.

- Lift upper barrel above lower barrel until hole in breakable rod coupling lines up with hole in upper rod.

- Install coupling pin and cotter pin to connect breakable rod coupling to upper hydrant rod.

Note:  Care should be taken to insure the upper barrel cannot fall during this operation.

- Turn operating nut in direction to close so that the upper barrel will lower onto the lower standpipe barrel.

- Place new breakable flange halves (flat side up) around the bottom of the hydrant barrel.

- Fasten to lower barrel flange using new bolts and nuts.

- Bleed air by slightly unscrewing one hose nozzle cap.  Check for gasket leaks by opening the operating nut until water starts to flow.  Tighten the hose nozzle cap and close the hydrant.

- The fire hydrant is now ready for service.