INSTALLATION INSTRUCTIONS FOR

EXTENSION USED ON WATEROUS PACER®

- Disassemble Fire Hydrant by:

  - Remove 4 bolts & nuts holding nozzle section to upper standpipe section.

Note:  The clamps should fall out.  However, they may have to be driven out.

  - Turn operating nut in direction to open so that nozzle section can be separated from upper standpipe section.  This will allow removal of nozzle section & upper operating nut.

  - Remove lower operating nut by unscrewing.

  - Remove support tube by lifting off.

  - Remove stop nut by unscrewing.

  - Remove support section by lifting off.

  - Remove bolts & nuts holding upper standpipe section to lower standpipe section.

  - Remove upper standpipe section by lifting off.

  - Remove upper stem by removing coupling nuts & breakable coupling halves.

- Reassemble Fire Hydrant by:

- Assemble rod extension to lower rod by placing the extension coupling halves on stud in lower rod & fasten with existing coupling nuts.  Use new coupling bolt & nut to fasten rod extension.

- Install extension flanges & snap rings on standpipe extension.

- Clean any dirt, pieces of gasket, etc. from machine surface on lower standpipe & extension standpipe.

- Place Extension gasket (flange down) on machine surface of lower standpipe.  (Use cement if desired).

- Place extension barrel on top of lower barrel.  Care should be taken to insure flange gasket is in proper place.

- Fasten extension standpipe to lower barrel using bolts & nuts provided with extension.

- The Hydrant is now ready to be reassembled by:

  - Assemble upper rod to rod extension by placing the breakage coupling halves on stud in upper rod & fasten with existing coupling nuts.  Use new coupling bolt & nut to fasten to rod extension.

  - Clean any dirt, pieces of gasket, etc. from machine surface on extension standpipe & bottom of upper standpipe.

  - Place extension gasket on machine surface of extension standpipe.  (Use cement if desired).

  - Place upper standpipe with 3/8” groove down on top of extension standpipe.  Care should be taken to ensure flange gasket is in proper place.

  - Fasten upper standpipe to extension standpipe using existing bolts & nuts.

  - Replace support gaskets in support section & reinstall.  Note:  Grease “O”-rings & support gaskets to assist in reinstallation.  Care should be taken to ensure “O”-rings are not damaged by the stem threads during reinstallation.

  - Install stop nut & tighten.

  - Install support tube by sliding down over stem until seated on support section.  Note:  Grease tube seal to assist in reinstallation ease of operation.

  - Install lower operating nut by tightening until hand tight.  Note:  Additional grease may be required on the threads of the upper rod.

  - Install nozzle section on upper standpipe section.  Note:  Make sure upper operating nut is engaged in lower operating nut.

  - Rotate nozzle section to proper direction.

  - Install bolts, nuts & clamps and tighten.

  - Check for gasket leaks by slightly unscrewing one nozzle cap and opening the hydrant valve until water starts to flow through the nozzle.  Close the cap and check for gasket leaks under pressure.  Close hydrant valve and open nozzle cap until the hydrant has drained, then retighten.

  - Tighten the hose nozzle cap & close hydrant.

  - The fire hydrant is now ready for service.