INSTALLATION INSTRUCTIONS FOR

EXTENSION USED ON WATEROUS TREND®

- Disassemble Fire Hydrant by:

  - Remove weather shield nut by driving out groove pin.

  - Remove 4 bolts & nuts holding upper standpipe section to lower standpipe section.

  - Remove nozzle section and upper standpipe section.

  - Remove breakable coupling halves by unscrewing nuts.

  - Inspect breakable coupling halves for hairline crack or other damage.  If damaged, replace with new breakable rod coupling.

- Reassemble Fire Hydrant by:

- Assemble rod extension to lower rod by placing the extension coupling halves on stud in lower rod & fasten with existing coupling nuts.  Use new coupling bolt & nut to fasten rod extension.

- Install extension flanges & snap rings on standpipe extension.

- Clean any dirt, pieces of gasket, etc. from machine surface on lower standpipe & extension standpipe.

- Place Extension gasket (flange down) on machine surface of lower standpipe.  (Use cement if desired).

- Place extension barrel on top of lower barrel.  Care should be taken to insure flange gasket is in proper place.

- Fasten extension standpipe to lower barrel using bolts & nuts provided with extension.

- The Hydrant is now ready to be reassembled by:

  - Assemble upper rod to rod extension by placing the breakage coupling halves on stud in upper rod & fasten with existing coupling nuts.  Use new coupling bolt & nut to fasten to rod extension.

Note:  Use new breakable rod coupling if existing ones are damaged.

  - Clean any dirt, pieces of gasket, etc. from machine surface on extension standpipe & bottom of upper standpipe.

  - Place extension gasket on machine surface of extension standpipe.  (Use cement if desired).

  - Lubricate “O” ring on operating nut.

  - Place nozzle section & upper standpipe section on top of extension standpipe.

  - Turn operating nut in direction to open until nozzle section and upper standpipe section is supported on thrust surface of operating nut.

  - Rotate nozzle section and upper standpipe section to desired direction.

  - Close operating nut until upper standpipe contact gasket on extension standpipe.

  - Fasten upper standpipe to extension standpipe using existing bolt & nut.

  - Install thrust bushing over operating nut.

  - Install weather shield nut on operating nut with groove pin.

  - Install bolts, nuts & clamps and tighten.

  - Check for gasket leaks by slightly unscrewing one nozzle cap and opening the hydrant valve until water starts to flow through the nozzle.  Close the cap and check for gasket leaks under pressure.  Close hydrant valve and open nozzle cap until the hydrant has drained, then retighten.

  - The fire hydrant is now ready for service.