INSTALLATION INSTRUCTIONS FOR

TRAFFIC REPAIR KITS USED ON WATEROUS TREND

WT-77®

- Disassemble Fire Hydrant by:

  - Remove weather cap (if equipped) by punching out retaining pin.

  - Separate upper stem and operating nut from upper barrel.

  - Remove broken flange, lock ring retaining lugs, flange gasket and lock ring from lower barrel at ground line and discard. Retain bury depth tag (if equipped).

  - Inspect upper and lower stems for damage, replace if necessary.

  - Remove breakable coupling halves from upper and lower stems and inspect coupling studs for damaged threads. If damaged, punch out studs for replacement with stainless steel bolts supplied in traffic kit.

- Reassemble Fire Hydrant by:

- Clean any dirt, pieces of gasket, etc. from machine surface on lower standpipe & upper standpipe.

- Install new breakable rod coupling on lower stem and fasten securely with bolt and brass locking nuts.

- Install new lock ring in groove on lower barrel.

- Install upper rod to breakable coupling and fasten securely with stainless bolt and brass locking nuts.(Be sure operating nut is screwed completely down onto the operating rod threads)

- Place flange gasket on cleaned surface of lower barrel. (Use cement if desired)

- Slide new breakable flange on to upper barrel and lower the upper barrel section on to the lower barrel aligning flange with lugs on hydrant.  Care should be taken to insure flange gasket is in proper place and the nozzles section is oriented correctly to the street curb.

- Place new lock ring retainer lugs so that the lip engages the lock ring on the lower barrel. Install a bolt and nut through each flange hole and lug. Replace bury depth tag and fasten bolts securely 60 to 70 lb-ft.

- Install weather cap on operating nut and secure with groove pin.

- Pressure Check Hydrant by:

  - Check for gasket leaks by slightly unscrewing one nozzle cap and opening the hydrant valve until water starts to flow through the nozzle.  Close the cap and check for gasket leaks under pressure.  Close hydrant valve and open nozzle cap until the hydrant has drained, then retighten.

  - The fire hydrant is now ready for service.