INSTALLATION INSTRUCTIONS FOR EXTENSION USED ON

AVK MODEL 2700® & MODEL 2780® FIRE HYDRANTS

- Disassemble fire hydrant by:

  - Remove the 4 bolts and nuts holding upper barrel to lower barrel.

  - Turn operating nut in direction to open so that upper barrel can be separated from lower barrel.

Note:  Care should be taken to insure the main valve does not open.  This is accomplished by applying upward pressure on the upper barrel while turning the operating nut.

  - Remove lower rod coupling pin and cotter pin.

Note:  Care should be taken to insure the upper barrel cannot fall during this operation.

  - Remove upper barrel and set aside.

  - Remove snap ring and breakable flange from lower barrel.

- The extension is now ready to be installed by:

  - Connect extension rod to extension coupling using a new clevis pin and cotter pin.

  - Fasten the extension rod assembly to the lower rod, lining up the second set of holes in the extension coupling and lower rod.

  - Install one extension flange and snap ring on lower barrel.

  - Install the second extension flange & snap ring on the extension barrel.

  - Clean any dirt, pieces of gasket, etc. from machined surface of lower barrel and extension barrel.

  - Place extension gasket on machined surface of lower barrel.

  - Place extension barrel (end with snap ring and flange) on top of lower barrel.

Note:  Care should be taken to insure gasket is in proper position.

  - Fasten extension barrel to lower barrel using new bolts and nuts.

3.	The hydrant is now ready to be reassembled by:

- Install snap ring and breakable flange on top end of extension barrel.

Note:  This is the ring and flange removed in Step 1 – E.

- Clean any dirt, etc. from machined surface of the extension barrel and bottom of upper barrel.

- Install new flange gasket on extension barrel.

- Place upper barrel above extension barrel and lower until hole in breakable rod coupling lines up with hole in rod extension.

- Install coupling pin and cotter pin to connect the breakable rod coupling to the rod extension.

Note:  Care should be taken to insure the upper barrel cannot fall during this operation.

- Turn operating nut in direction to close so that upper barrel will lower onto extension barrel.

- Fasten upper barrel to extension barrel using existing bolts & nuts.

- Check for gasket leaks by slightly unscrewing one nozzle cap and opening the hydrant valve until water starts to flow through the nozzle.  Close the cap and check for gasket leaks under pressure.  Close hydrant valve and open nozzle cap until the hydrant has drained, then retighten.

- The fire hydrant is now ready for service.