INSTRUCTIONS FOR INSTALLING TRAFFIC REPAIR KIT USED ON

5-1/4” AVK MODEL 2700® & MODEL 2780® FIRE HYDRANTS

- Disassemble fire hydrant by:

  - Isolate the hydrant from the main water supply.

  - Remove bolts and nuts that hold upper barrel to lower barrel.  The upper barrel may be completely separated due to vehicle impact.

  - Check all above-ground hydrant parts to insure they are in good working condition.

  - Turn operating nut, in the direction to open, until upper rod coupling, clevis pin and cotter pin can be easily reached.

  - Remove and discard the cotter pin, clevis pin, and top half of te broken stem rod coupling.

  - Remove and discard the cotter pin, lower pin, and bottom half of the broken stem rod coupling on the lower stem.

Note:  Care should be taken to prevent any of these parts from falling into the lower barrel.

  - Remove and discard standpipe gasket, breakable flange, and snap ring.

Note:  The flange will probable be broken in several pieces.

- The hydrant is now ready to be reassembled by:

  - Install the stem rod coupling to the lower rod using a new lower pin and cotter pin.

  - Install the snap ring and breakable flange (flange up) on the top of the lower barrel.

  - Clean any debris from machine surface of lower barrel.

  - Install new flange gasket on lower barrel.

Note:  Care should be taken to insure flange gasket is centered over lower barrel surface.

  - Lift upper barrel above lower barrel until hole in breakable rod coupling lines up with hole in upper rod.

  - Install clevis pin and cotter pin to connect breakable rod coupling to upper rod.

Note:  Care should be taken to insure the upper barrel cannot fall during this operation.

  - Turn operating nut in direction to close so that the upper barrel will lower onto the standpipe barrel.

  - Fasten upper barrel flange to new breakable flange using new bolts and nuts.

  - Check for gasket leaks by slightly unscrewing one nozzle cap and opening the hydrant valve until water starts to flow through the nozzle.  Close the cap and check for gasket leaks under pressure.  Close hydrant valve and open nozzle cap until the hydrant has drained, then retighten.

  - The fire hydrant is now ready for service.