INSTALLATION INSTRUCTIONS FOR EXTENSIONS

USED ON

CLOW EDDY® FIRE HYDRANTS

- Disassemble upper barrel (nozzle section) of fire hydrant by:

  - Remove hold-down nut.

  - Lift off operating nut.

  - Remove packing nut.

  - Remove bonnet (cap cover) bolts and nuts.  Then remove bonnet and swivel ring.

  - Remove drain lever pin and lever, then lift out drain support.

  - Remove drain rod by lifting out.

  - Remove upper barrel (nozzle section), bolts and nuts, then remove upper barrel.

  - Remove upper stem and breakable coupling by removing lower coupling pin or bolt in breakable coupling.

- The extension is now ready to be installed by:

  - Assemble extension stem to extension coupling using 3/8” diameter bolt and nut.

  - Now fasten the extension stem assembly to the lower stem through the second set of holes in the extension coupling using the second 3/8” diameter bolt and nut.

  - Clean any dirt, pieces of gasket, etc. from machined surface of lower barrel and extension barrel.

  - Place extension gasket on machined surface of lower barrel.

  - Place extension barrel on top of lower barrel.  Care should be taken to insure extension gasket is in proper place and that the extension is centered over the lower barrel.

  - Fasten extension barrel to lower barrel using bolts proved with extension.

  - Assemble the extension drain rod to the drain rod.  Care should be taken to insure the drain rod is extended the same length as extension length 6”, 12”, 18”, 24” etc.

- The upper barrel is now ready to be assembled by:

  - Assemble upper stem assembly (stem and breakable coupling) to the extension stem through the second set of holes in the safety coupling using the existing pin or bolt.

  - Clean any dirt, pieces of gasket, etc. from machined surface of extension and nozzle section.

  - Place extension gasket on top of machined surface of extension.

  - Place nozzle section on top of extension barrel.  Care should be taken to keep gasket in place while centering nozzle section.

  - Bolt nozzle section to extension barrel using existing flanges, bolts and nuts.

  - Clean any dirt, pieces of gasket, etc. from nozzle section, bonnet and swivel ring.

  - Install gasket on top of nozzle section, then install swivel ring.

  - Install drain rod into cup.  Make sure the drain valve is in the cup by pushing down and twisting.

  - The spool on the upper end of drain rod should be level with swivel ring.

  - Replace drain lever into clevis and fasten with drain lever pin.  The forked end slides on the drain rod spool.

  - Center the main stem, push stem wedge against main stem and tighten screw.

  - The curved end of drain lever is flat as it rides against main stem.  If not, repeat Step K.

  - The drain rod should travel from open to closed approximately 3/8”.  If not, adjust spool.

  - Clean any dirt, pieces of gasket, etc. from nozzle section and bonnet (cover cap).

  - Replace gasket, and then place bonnet on nozzle section.  Make sure “Open” is directly over inlet.

  - Replace bonnet bolts and nuts.

  - Replace operating nut and hold down nut.  Tighten hold down nut.

  - Check for gasket leaks by slightly unscrewing one nozzle cap and opening the hydrant valve until water starts to flow through the nozzle.  Close the cap and check for gasket leaks under pressure.  Close hydrant valve and open nozzle cap until the hydrant has drained, then retighten.

  - To check the drain valve, open nozzle cap and see if water is draining properly.  If so, replace and tighten the hose nozzle cap.

  - The fire hydrant is now ready for service.