INSTALLATION INSTRUCTIONS FOR EXTENSION

USED ON

CLOW MEDALLION™ FIRE HYDRANTS

- Disassemble Upper Barrel of Fire Hydrant by:

  - Remove from the bonnet; the weather cap, hold-down nut, anti-friction washer, operating nut and optional stem jam nut if equipped. (Note: remove H/D Nut by turning clockwise).

  - If using a brass sleeve, lubricate outside and slide over upper stem threads to protect O-ring when removing bonnet.

  - Remove bolts between bonnet and upper barrel and remove the bonnet.

  - Remove safety flange bolts between upper barrel and lower barrel, and then remove upper barrel and safety flanges.

  - Remove the lower cotter pin and clevis pin on the safety stem coupling to remove the upper stem and safety stem coupling.

- The Extension is now ready to be installed by:

  - Assemble extension stem to extension coupling using clevis pin and cotter pin.

  - Now fasten the extension stem assembly to the lower stem through the second set of holes in the extension coupling using the clevis pin and cotter pin.

  - Clean any dirt, pieces of gasket, etc. from the machine surface of lower barrel before placing lower O-ring in place.

  - Place extension barrel (flange end) on top of lower barrel.  Care should be taken to insure lower O-ring is in proper place.

  - Hold flange halves in place and bolt extension barrel to lower barrel.  Make sure to use the solid flange halves and not the safety flange halves, which are grooved.

3.	The Upper Barrel is now ready to be reassembled by:

- Assemble upper stem to safety stem coupling using the clevis pin and cotter pin.  The arrow on the safety stem coupling should be pointed toward the upper stem.  Note:  the upper stem assembly (upper stem and safety stem coupling) should already be assembled.

- Now fasten the upper stem assembly to the extension stem through the second set of holes in the safety stem coupling using the clevis pin and cotter pin.

- Clean any dirt, etc. from machined surface of extension barrel before placing upper O-ring in place.

- Place upper barrel on top of extension barrel.  Care should be taken to insure upper O-ring in proper place.

- Hold safety flange halves in place and bolt the upper barrel to extension barrel.  Make sure they are safety flange halves, which are grooved.

- Clean any dirt, etc. from upper barrel before placing bonnet gasket in place.

- If using brass sleeve, place over upper stem threads and lubricate to protect O-ring when installing bonnet.

- Place bonnet on upper barrel and hand tighten bolts.

- Remove brass sleeve and then assemble optional jam nut if equipped, operating nut, anti-friction washer, hold-down nut and weather cap.  Care should be taken to insure O-ring seals are against shoulder on outside of hold-down nut and on inside groove when contacting operating nut.

- Remove oil plug in bonnet and fill with lubricant until level with oil plug hole.  Replace oil plug.

- Tighten bonnet bolts.

- Bleed air by slightly unscrewing one hose nozzle cap.  Check for gasket leaks by opening the hydrant until water starts to flow.  Tighten the hose nozzle cap and close the hydrant.  Remove nozzle cap until barrel is drained and then replace hose nozzle cap.

- The fire hydrant is now ready for service.