INSTALLATION INSTRUCTIONS FOR EXTENSION USED ON

KENNEDY® K81A® & K81D® FIRE HYDRANT

- Disassemble upper standpipe of fire hydrant without stop nut by:

  - Remove cap bolts & nuts.

  - Remove cap assembly by turning operating nut in direction to open until cap assembly is free of upper stem.

  - Remove upper standpipe by removing breaking ring bolts & nuts and breaking ring & lifting over upper stem.

  - Remove upper stem & breaking coupling by removing lower coupling pin.

- The extension is now ready to be installed by:

  - Assemble extension stem (use hole closest to end of stem – approximately 5/8”) to extension coupling (use rounded end of coupling with hole approximately 1’ from end) using clevis pin & cotter pin.

  - Now fasten the extension stem assembly to the lower stem through the second set of holes in the extension coupling using a second clevis pin & cotter pin.

  - Clean any dirt, pieces of gasket, etc. from machine surface of lower barrel.

  - Place extension gasket on machine surface of lower barrel.

  - Place extension barrel (spool) on top of lower barrel.  Care should be taken to ensure flange gasket is in proper place & that bolt holes between lower barrel & extension barrel are lined up.

  - Fasten extension barrel to lower barrel using bolts provided with extension kit.

3.	The upper barrel is now ready to be reassembled by:

- Assemble upper stem to breaking stem coupling using upper coupling pin.  Note:  The upper stem assembly (upper stem & breaking stem coupling) should already be assembled.

- Now fasten the upper stem assembly to the extension stem using the lower coupling pin & fasten with hair pin clip.

- Clean any dirt, etc. from machined surface of the extension barrel & bottom of upper barrel.

- Install new square “O” ring in the bottom of upper barrel & place on top of extension barrel.  Note:  Use grease to hold “O” ring in place.

- Install existing breaking ring flanges.  Install bolts & nuts and tighten.

- Place cap assembly over upper stem & turn in direction to close hydrant.  Note:  Care should be taken to ensure the “O” rings are not damaged.

- Align cap flange bolt holes with upper barrel bolt holes & install cap bolts & nuts and tighten.

- Check for gasket leaks by slightly unscrewing one nozzle cap and opening the hydrant valve until water starts to flow through the nozzle.  Close the cap and check for gasket leaks under pressure.  Close hydrant valve and open nozzle cap until the hydrant has drained, then retighten.

- Fire hydrant is now ready for service.