INSTALLATION INSTRUCTIONS FOR

COLLISION REPAIR KIT USED ON

KENNEDY® K81a® FIRE HYDRANT

- Disassemble upper standpipe of fire hydrant by:

  - Remove cap bolts and cap.

  - Remove cap assembly by turning operating nut in direction to open until cap assembly is free of upper stem.

  - Drive out upper coupling pin to separate upper stem from broken stem breaking coupling.

  - Remove bolts & nuts holding broken standpipe breaking ring to upper barrel (standpipe).

- Prepare lower barrel by:

  - Remove hair pin clip from lower coupling pin.

  - Remove lower coupling pin, then remove broken stem breaking coupling from the lower stem.

  - Remove any broken material, etc. that may have fallen into lower barrel (standpipe).

  - Clean any dirt, etc. from machine surface of lower barrel.

3.	The hydrant is now ready to be reassembled by:

- Assemble upper stem to stem breaking coupling using new clevis and cotter pin.

- Now fasten the upper stem assembly to the lower stem through the second set of holes in stem breaking coupling using clevis pin & cotter pin.

- Clean any dirt, etc. from machine surface of upper barrel.

- Install new square “O” ring in the bottom of upper barrel (standpipe) & place on top of lower barrel (standpipe).  Use grease to hold “O” ring in place.

Note:  Make sure the upper barrel is facing desired direction.

- Install new standpipe breaking ring flanges using new bolts & nuts, then tighten.

- Replace cap gasket on top of upper barrel (standpipe).

Note:  Care should be taken to insure the “O” rings are not damaged.

- Place cap assembly over upper stem & turn in direction to close hydrant.

- Check for gasket leaks by slightly unscrewing one nozzle cap and opening the hydrant valve until water starts to flow through the nozzle.  Close the cap and check for gasket leaks under pressure.  Close hydrant valve and open nozzle cap until the hydrant has drained, then retighten.

- The fire hydrant is now ready for service.