INSTALLATION INSTRUCTIONS

FOR TRAFFIC REPAIR KIT USED ON

M&H® 129® FIRE HYDRANT

- Disassemble upper barrel (nozzle section) of fire hydrant by:

  - Remove from the bonnet the operating lock nut by turning in opposite direction of hydrant opening.

  - Unscrew operating nut.

  - Remove bonnet bolts & nuts, then remove bonnet.

  - Install thin sleeve over stem threads to protect “O” rings when removing seal plate.

  - Remove seal plate bolts & nuts, then remove seal plate & seal plate gasket.

  - Remove upper part of broken stem coupling from upper stem by removing the stem coupling bolt & nut and discard.

  - Remove any remaining breakable bolts & nuts from upper barrel & discard.

  - Inspect upper barrel from damage.

- Prepare lower barrel by:

  - Remove lower part of broken stem coupling from lower stem by removing the stem coupling bolt & nut and discard.

  - Inspect & remove any foreign material that may have fallen into the lower barrel.

3.	The upper barrel is now ready to be reassembled by:

- Assemble upper stem to round end of stem breakable coupling with existing bolt & nut.

Note:  The breakable stem coupling on 5-1/4” may have one end round & one end square.  The upper end is rounded.

- Assemble upper stem assembly to lower stem through holes in the lower end of breakable stem coupling using new bolt & nut.

- Clean any dirt, pieces of gasket, etc. from flange surface of extension & upper barrel.

- Place standpipe gasket & then upper barrel on lower barrel.  Care should be taken to insure gasket is in proper place.

- Bolt upper barrel to lower barrel with new breakable bolts & nuts.

- Using thin sleeve over upper stem to protect “O” ring, install seal plate & gasket with existing bolts & nuts.

- Remove thin sleeve & grease threads on upper stem.

- Install bonnet with existing bolts & nuts.

- Install operating nut & locking nut.

- Check for gasket leaks by slightly unscrewing one nozzle cap and opening the hydrant valve until water starts to flow through the nozzle.  Close the cap and check for gasket leaks under pressure.  Close hydrant  valve and open nozzle cap until the hydrant has drained, then retighten.

- The fire hydrant is now ready for service.