INSTALLATION INSTRUCTIONS FOR EXTENSION

USED ON M&H® 6-129® or 129® FIRE HYDRANT

USING 6-129® NEW STYLE EXTENSION

- Disassemble upper barrel (nozzle section) of fire hydrant by:

  - Remove operating nut/weather cap by removing set screw (M&H 6-129 new style only).

  - Remove from the bonnet the operating lock nut by turning in opposite direction of hydrant opening.

  - Unscrew operating nut.

  - Remove bonnet bolts & nuts, then remove bonnet.

  - Install thin sleeve over stem threads to protect “O” rings when removing seal plate.

  - Remove seal plate bolts & nuts, then remove seal plate & seal plate gasket.

  - Remove the bolts & nuts and safety flanges holding upper barrel (nozzle section) to standpipe, then remove upper barrel.

Note:  There are no safety flanges on M&H 129 old style.

  - Remove upper stem & breakaway coupling as an assembly by removing bolt & nut holding breakaway coupling to lower stem.

- The extension is now ready to be installed by:

  - Assemble extension stem to extension coupling (non breakaway) using 3/8” bolt & nut.

  - Now fasten the extension stem assembly to the lower stem through the second set of holes in the extension coupling using the second 3/8” bolt & nut.

  - Clean any dirt, pieces of gasket, or “O” ring etc. from flange surface of lower barrel (standpipe).

  - Place standard flat gasket and then extension barrel on lower barrel.  Care should be taken to insure gasket is in proper place.

  - Bolt extension to lower barrel using non-breakable bolts & nuts and extension flanges from extension kit.

Note:  Make sure not to use breakable bolts between lower barrel and extension.

Note:  For old hydrants without removable safety flanges, this is a flange to flange connection. You will use the extension flanges with BREAKABLE BOLTS to connect the top of the extension to the upper standpipe see (3:E below).

3.	The upper barrel is now ready to be reassembled by:

- Assemble upper stem to round end of stem breakable coupling with existing bolt & nut.

Note:  The upper stem assembly should already be assembled.

- Assemble upper stem assembly (stem & stem breakable coupling) to extension stem through holes in the square end of breakable coupling with existing bolt & nut.

Note:  Breakable coupling may be round on both ends.

- Clean any dirt, pieces of gasket, or “O” ring etc. from flange surface of extension & upper barrel.

- Place upper barrel and “O” ring on standpipe extension.  Care should be taken to insure “O” ring is in proper place.

Note:  Use flat gasket on 129 old style.

- Bolt upper barrel to extension using the existing bolts & nuts and safety flanges.

Note:  When installing on M&H 129 old style, use breakable bolts & nuts with extension flanges.

- Using thin sleeve over upper stem to protect “O” ring, install seal plate & gasket with existing 3 bolts & nuts.

- Remove thin sleeve & grease threads on upper stem.

- Install bonnet with existing bolts & nuts.

- Install operating nut & locking nut.

- Check for gasket leaks by slightly unscrewing one nozzle cap and opening the hydrant valve until water starts to flow through the nozzle.  Close the cap and check for gasket leaks under pressure.  Close hydrant valve and open nozzle cap until the hydrant has drained, then retighten.

- The fire hydrant is now ready for service.