INSTALLATION INSTRUCTIONS FOR EXTENSION USED ON

M&H® 929® FIRE HYDRANT

- Disassemble upper barrel (nozzle section) of fire hydrant by:

  - Remove weather shield bolt with Allen wrench.

  - Remove weather shield by lifting off.

  - Unscrew stem nut lock nut with lock nut wrench – turn in opposite direction of hydrant opening.

  - Unscrew stem nut.

  - Remove the bonnet & gasket by removing the 3 bonnet bolts & nuts.

  - Unscrew stem stop nut – turn in same direction as hydrant opening.

  - Install thin sleeve over stem threads to protect “O” ring when removing seal plate.

  - Remove seal plate & gasket by removing the 3 seal plate bolts & nuts.

  - Remove 6 bolts & nuts holding the breakaway lugs, then remove upper barrel.

  - Remove upper stem & breakaway coupling as an assembly by removing bolts & nuts holding breakaway coupling to lower stem.

- The extension is now ready to be installed by:

  - Assemble extension stem to extension coupling (non breakaway) using 3/8” bolt & nut.

  - Now fasten the extension stem assembly to the lower stem through the second set of holes in the extension coupling using the second 3/8” bolt & nut.

  - Clean any dirt, pieces of gasket, etc. from flange surface of lower barrel (standpipe) & flange end of standpipe coupling.

  - Fill ring gasket groove (flange end of standpipe coupling) with grease such as automobile wheel bearing grease.

  - Press ground flange joint ring gasket “O” ring into grease.

  - Place standpipe extension *flange end) on lower barrel.  Care must be taken to insure ring gasket is in proper place while centering the standpipe extension over lower barrel.

  - Hold non-breakaway lugs (one at a time) in place & bolt standpipe extension to lower barrel.  Make sure to use the non-breakaway lugs which are larger than the breakaway lugs.

3.	The upper barrel is now ready to be reassembled by:

- Assemble upper stem to round end of stem breakable coupling with existing bolt & nut.

Note:  The upper stem assembly should already be assembled.

- Assemble upper stem assembly (stem & stem breakable coupling) to extension stem through holes in the square end of breakable coupling with existing bolt & nut.

- Clean any dirt, etc. from machine surface of standpipe extension & flange end of upper barrel.

- Fill ring gasket groove on flange end of upper barrel with grease.

- Press ground flange joint ring gasket “O” ring into grease.

- Place upper barrel on standpipe extension.  Care must be taken to insure ring gasket is in proper place while centering the upper barrel on the standpipe extension.

- Hold breakaway lugs (one at a time) in place & bolt upper barrel to standpipe extension.

- Using thin sleeve to protect “O” ring, install seal plate & gasket with existing 3 bolts & nuts.

- Remove thin sleeve & grease threads on upper stem & stem nut.

- Install stem stop nut.  Screw to the lower end of upper stem & tighten to 10 to 20 foot pounds torque.

- Install bonnet & gasket with existing 3 bolts & nuts.

- Install stem nut by screwing onto upper stem.

- Install thrust washer to top of stem nut, then screw stem nut lock nut in place & tighten with lock nut wrench.

- Install weather shield with weather shield bolt.

- Check for gasket leaks by slightly unscrewing one nozzle cap and opening the hydrant valve until water starts to flow through the nozzle.  Close the cap and check for gasket leaks under pressure.  Close hydrant valve and open nozzle cap until the hydrant has drained, then retighten.

- The fire hydrant is now ready for service.