INSTALLATION INSTRUCTIONS FOR TRAFFIC REPAIR KITS

USED ON M&H® 929® FIRE HYDRANT

- Disassemble upper barrel (nozzle section) of fire hydrant by:

  - Remove weather shield bolt with Allen wrench.

  - Remove weather shield by lifting off.

  - Unscrew stem nut lock nut – turn in opposite direction of hydrant opening.

  - Remove operating stem nut.

  - Remove bonnet bolts & nuts and lift bonnet off.

  - Unscrew stem stop nut – turn in same direction as hydrant opening.

  - Now remove upper rod and seal plate.

  - Remove broken pieces of stem coupling from upper and lower stem.

  - Remove old bolts and breakaway lugs from upper barrel flange and clean flange gasket surfaces on upper and lower barrels.

  - Inspect upper and lower barrel flange areas for possible damage, if damaged replace barrel.

- The traffic kit is now ready to be installed by:

  - Assemble new safety stem coupling to lower stem using 3/8” bolt & nut.

  - Now fasten the upper stem into the top of the safety coupling using the second 3/8” bolt and nut.

  - Fill ring gasket groove on flange end of upper barrel with grease such as automotive wheel bearing grease or hydrant grease.

  - Press ground flange joint ring gasket O- ring into grease.

  - Place upper barrel onto lower barrel. Care must be taken to insure O-ring gasket is in proper place while centering the upper barrel onto the lower barrel.

  - Connect the upper and lower barrels together using new break lugs and bolts and nuts - insure that all lugs make contact with the small flange on the lower barrel.

  - Grease threads on upper stem, stem nut & stem nut lock nut.

  - Clean gasket surfaces on seal plate & upper barrel and install seal plate with new flat gasket.

  - Screw the stem stop nut down to the sleeve of upper stem & tighten to 10 to 20 foot pounds torque.

  - Place second flat gasket on top of seal plate and fasten bonnet to upper barrel with existing bonnet bolts and nuts.

  - Install stem nut onto upper stem.

  - Screw stem nut lock nut tightly back into the bonnet.

  - Install weather shield with weather shield bolt.

  - Check for gasket leaks by slightly unscrewing one nozzle cap and opening the hydrant valve until water starts to flow through the nozzle. Close the cap and check for gasket leaks under pressure. Close hydrant valve and open nozzle cap until the hydrant has drained, then retighten.

  - The fire hydrant is now ready for service.