INSTALLATION INSTRUCTIONS FOR EXTENSION USED ON

MUELLER IMPROVED™ (BEFORE 1972) FIRE HYDRANTS

- Disassemble Upper Barrel of Fire Hydrant by:

  - Remove from the bonnet the weather cap, hold-down nut, anti-friction washer and operating nut.  (Note: H/D Nut unscrews in the opposite direction of “Open”).

  - If using a brass sleeve, lubricate outside and slide over upper stem threads to protect “O” ring when removing bonnet.

  - Remove bolts between bonnet and upper barrel and remove bonnet.

  - Remove safety flange bolts between upper barrel and lower barrel, and then remove upper barrel and safety flanges.

  - Remove the safety sleeve from the upper stem by loosening the set screw.

  - Remove the safety coupling (thimble) by unthreading from the upper and lower rods.

- The Extension is now ready to be installed by:

  - Clean any dirt, pieces of gasket, etc. from the machine surface of lower barrel before placing               flange gasket in place.

  - Thread brass extension coupling onto lower rod (set screw hole UP) until tab of lower rod can be seen through set screw hole.

  - Next thread the slotted end of extension rod into extension coupling until it just matches up with the tab of lower rod seen through the set screw hole.

  - Hold extension rod stationary and screw the extension coupling up until the rods are solidly connected. Pin with the set screw provided with the coupling.

  - Place extension barrel (flange end) on top of lower barrel. Care should be taken to insure                     flange gasket is in proper place.

  - Hold flange halves in place and bolt extension barrel to lower barrel. Make sure to use the solid flange halves and not the safety flange halves, which are grooved.

3.	The Upper Barrel is now ready to be reassembled by:

- Now slide the safety sleeve onto upper stem (set screw hole UP) install safety coupling (same procedure as extension coupling above). Match tabs in safety sleeve with slots in safety coupling and pin with set screw.

- Clean any dirt, etc. from the machined surface of lower barrel before placing flange gasket / O-ring in place.

- Place upper barrel on top of extension barrel. Care should be taken to insure flange gasket / O-ring is in proper place.

- Hold grooved safety flange halves in place and bolt upper barrel to extension barrel.

- Clean any dirt, etc. from upper barrel before placing bonnet gasket / O-ring in place.

- If using brass sleeve, place over upper stem threads and lubricate to protect stem O-rings when installing bonnet.

- Place bonnet on upper barrel and hand tighten bolts.

- Remove brass sleeve and then assemble operating nut, antifriction washer, hold-down nut and weather cap.  Care should be taken to insure O-ring seals are at threaded shoulder on outside of hold-down nut & on inside when contacting operating nut.

- Remove oil plug in bonnet and fill with lubricant until level with oil plug hole.  Replace oil plug.

- Tighten bonnet bolts.

- Bleed air slightly unscrewing one hose nozzle cap. Check for gasket leaks by opening the hydrant until water starts to flow. Tighten the hose nozzle cap and close the hydrant.  Remove nozzle cap until barrel is drained and then replace hose nozzle cap.

- Fire Hydrant is now ready for service.