INSTALLATION INSTRUCTIONS FOR SAFETY FLANGE KIT

USING BRASS SAFETY COUPLING

MUELLER IMPROVED™ (BEFORE 1972)

- Disassemble Upper Barrel of Fire Hydrant by:

  - Remove from the bonnet the weather cap, hold-down nut, anti-friction washer and operating nut.   (Note: H/D Nut unscrews in the opposite direction of “Open”).

  - If using a brass sleeve, lubricate outside and slide over upper stem threads to protect the O-ring when removing bonnet.

  - Remove bolts between bonnet and upper barrel and remove bonnet.

  - Remove safety flange bolts and broken safety flanges from upper barrel.

  - Remove the old safety sleeve (thimble) from the upper stem by loosening the set screw.

- Prepare Lower Barrel by:

  - Remove the damaged brass safety stem coupling from lower stem.

  - Remove any broken coupling material, etc. that may have fallen into the lower barrel.

3.	The Upper Barrel is now ready to be reassembled by:

- Assemble upper stem by screwing round brass safety stem coupling all the way down on lower stem.  Loosen until tongue is visible and aligned through eyelet hole.

- Screw upper stem into upper end of round brass safety stem coupling until finger tight against lower stem.  Loosen upper stem until groove aligns with tongue on lower stem.  Hold upper stem and rotate brass safety coupling (counter clockwise) until tight, then tighten set screw.

- Clean any dirt, etc. from machined surface of lower barrel before placing flange gasket in place.

- Place upper barrel on top of lower barrel.  Care should be taken to insure flange gasket is in proper place.

- Hold grooved safety flange halves in place and bolt upper barrel to lower barrel.

- Clean any dirt, etc. From upper barrel before placing bonnet gasket in place.

- If using brass sleeve, place over upper stem threads and lubricate to protect O-ring when installing bonnet.

- Place bonnet on upper barrel and hand tighten bolts.

- Remove brass sleeve and then assemble operating nut, anti-friction washer, hold-down nut and weather cap.  Care should be taken to insure O-ring seals are at threaded shoulder on outside of hold-down nut and on inside when contacting operating nut.

- Remove oil plug in bonnet and fill with lubricant until level with oil plug hole.  Replace oil plug.

- Tighten bonnet bolts.

- Bleed air by slightly unscrewing one hose nozzle cap.  Check for gasket leaks by opening the hydrant until water starts to flow.  Tighten the hose nozzle cap and close the hydrant.  Remove nozzle cap until barrel is drained and then replace hose nozzle cap.

- Fire hydrant is now ready for service.