INSTALLATION INSTRUCTIONS FOR TRAFFIC REPAIR KITS USED ON

US PIPE H SERIES® 4-5/8” 200 & 5-1/4” 205

FIRE HYDRANTS

- Disassemble nozzle section of fire hydrant by:

  - This repair can be made with water pressure on as long as the lower rod and main valve seat are not damaged.

  - Remove bolts and nuts and broken flange form upper and lower barrel. The upper barrel may be completely separated due to vehicle impact.

  - Check all hydrant parts above ground to insure they are in good working condition.

  - Turn operating nut in the direction of open until upper rod coupling, and pins can be easily reached.

  - Remove and discard the pins and top half of the broken rod coupling from the upper stem.

  - Remove and discard the pins and bottom half of the broken rod coupling from the lower stem.

  - Care should be taken to prevent any of these parts from falling into the lower barrel.

  - Remove and discard standpipe o-ring.

- Reassemble Fire Hydrant by:

  - Install new breakable coupling to hydrant lower rod and secure with new stainless steel bolt and nut provided.

  - Clean debris from o-ring groove and surface of lower barrel and install new flange o-ring.

  - Lower nozzle section of hydrant down over lower barrel until hole in breakable coupling lines up with hole in upper rod.

NOTE:  Care should be taken to insure upper barrel cannot fall during this operation.

  - Secure the coupling to upper rod with stainless steel bolt and nut provided.

  - Turn operating nut in direction to close so that the upper barrel will make contact with  lower standpipe.

  - Fasten upper barrel to lower barrel with new safety flanges and 8 zinc bolts and nuts provided.

Note: be careful to fasten the bolts evenly so the flanges pull together evenly otherwise flanges may be pinched causing them to break.

  - Check for gasket leaks by slightly unscrewing one nozzle cap and opening the hydrant valve until water starts to flow through the nozzle. Close the cap and check for gasket leaks under pressure. Close hydrant valve and open nozzle cap until the hydrant has drained, then retighten.

  - The fire hydrant is now ready for service.