INSTALLATION INSTRUCTIONS FOR TRAFFIC REPAIR KITS USED ON

US PIPE MET-250® AND MET-250 M94®

FIRE HYDRANTS

- Disassemble nozzle section of fire hydrant by:

  - This repair can be made with water pressure on as long as the lower rod and main valve seat are not damaged.

  - Remove bolts and nuts and broken flange form upper and lower barrel. The upper barrel may be completely separated due to vehicle impact.

  - Check all hydrant parts above ground to insure they are in good working condition.

  - Turn operating nut in the direction of open until upper rod coupling, coupling pin and cotter pin can be easily reached.

  - Remove and discard the pins and top half of the broken rod coupling from the upper stem.

  - Remove and discard the pins and bottom half of the broken rod coupling from the lower stem.

  - Care should be taken to prevent any of these parts from falling into the lower barrel.

  - Remove and discard standpipe o-ring.

- Reassemble Fire Hydrant by:

  - Install new breakable coupling to hydrant lower rod and secure with new stainless steel clevis and cotter pin.

  - Install dampener o-ring inside of breakable coupling so that it rests on top of lower stem.(M94 model only)

  - Clean debris from o-ring groove and surface of lower barrel and install new flange o-ring.

  - Lower nozzle section of hydrant down over lower barrel until hole in breakable coupling lines up with hole in upper rod.

NOTE:  Care should be taken to insure upper barrel cannot fall during this operation.

  - Secure the coupling to upper rod with stainless steel clevis pin and cotter pin provided.

  - Turn operating nut in direction to close so that the upper barrel will lower onto the lower standpipe barrel.

  - Fasten upper barrel to lower barrel with new safety flanges and stainless steel bolts provided.

Note: be careful to fasten the bolts back and forth evenly so the flanges pull together evenly otherwise flanges may be pinched causing them to break.

  - Check for gasket leaks by slightly unscrewing one nozzle cap and opening the hydrant valve until water starts to flow through the nozzle. Close the cap and check for gasket leaks under pressure. Close hydrant valve and open nozzle cap until the hydrant has drained, then retighten.

  - The fire hydrant is now ready for service.