INSTRUCTIONS FOR INSTALING EXTENSION KITS ON

EAST JORDAN WATERMASTER® 5BR250® AND CD250® HYDRANTS

- Disassemble Upper Barrel of Fire Hydrant by:

  - Remove from the bonnet the hold-down nut and operating nut.

  - Remove bolts between bonnet and upper barrel and remove bonnet.

  - Remove 6 safety flange bolts between upper barrel and lower barrel, and then remove 6 BOLT upper barrel and safety flanges (3 BOLT HOLES EACH HALF). These flanges must be reinstalled to upper barrel.

  - Remove the lower cotter pin and clevis pin on the safety coupling to remove the upper stem and safety stem coupling.

- The Extension is now ready to be installed by:

NOTE: EXTENSION FLANGES MUST BE INSTALLED TO EXTENSION BARREL ONLY!

  - Assemble extension stem to extension coupling using clevis pin and cotter pin.

  - Now fasten the extension stem assembly to the lower stem through the second set of holes in the extension coupling using clevis pin and cotter pin.

  - Clean any dirt, pieces of gasket, etc. from the machine surface of lower barrel.

  - Place extension barrel (8 BOLT flanged end) on top of lower barrel. Care should be taken to ensure O-ring is in proper place.

  - Line up extension flange halves (4 BOLT HOLES EACH HALF) underneath extension and fasten 8 BOLT extension barrel to lower barrel. ONLY the flanges included with the extension kit will fit at this connection.

  - Grease O-ring and place in groove on top of extension barrel.

3.	The Upper Barrel is now ready to be reassembled by:

- Assemble upper stem to safety stem coupling using clevis pin and cotter pin. Note: The upper stem assembly (upper stem and safety stem coupling should already be assembled).

- Now fasten the upper stem assembly to the extension stem through the second set of holes in the safety stem coupling using clevis pin and cotter pins.

- Place 6 BOLT upper barrel on top of extension barrel. Care should be taken to ensure flange gasket/O-ring is in proper place.

- Hold safety flange halves (3 BOLT HOLES EACH HALF) underneath 6 BOLT upper barrel and fasten to top of extension barrel.

- Clean any dirt, etc. from upper barrel before placing bonnet O-ring in place.

- Place bonnet on upper barrel and hand tighten bolts.

- Lube upper rod threads and assemble operating nut, and hold-down nut.

- Tighten bonnet bolts.

- Bleed air slightly unscrewing one hose nozzle cap. Check for gasket leaks by opening the operating nut until water starts to flow. Tighten the hose nozzle cap and close operating nut.  Remove nozzle cap until barrel is drained and then replace hose nozzle cap.

- Fire Hydrant is now ready for service.